## 2.1. - Tab. 1,2
Basic technical parameters – Nhouse-300 (NH1-030-ECS0HRxAS-xA0) – heat exchanger
Tab. 1
Nhouse type |  |  | NH1-30-ECS0HRXAS-0A0 | NH1-30-ECS0HRPAS-0A0 | NH1-30-ECS0HRXAS-1A0 | NH1-30-ECS0HRPAS-1A0
Bypass version |  |  | Electronic |  | Mechanical
Unit equipment - preheater |  |  | - | electric | - | electric
Nominal air output* / BOOST** |  | m3/hour | 300/310 |  | 270/290
Noise level** |  | dB(A) | 43.3 |  | 42
Weight**** |  | kg | 16.1 | 17.2 | 16 | 17
Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
Nominal unit power consumption* / BOOST** |  | W | 184/195 | 784/795 | 180/182 | 780/782
Nominal unit current* / BOOST** |  | A | 1.44/1.52 | 4.04/4.12 | 1.4/1.4 | 4/4
Recuperation efficacy ***** |  | % | 81 |  | 80.5
Protection type |  | IP | 20
Energy efficiency ratio (ERP) |  |  | cold climate A+, medium climate A, warm climate A
* Nominal air output (power, current) at an external pressure drop of 150 Pa
** BOOST regime - maximum intense ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
*** Sound pressure level in free space at the distance of 3 m
**** Unit weight without packaging
***** Recuperation efficiency per EN 308
Basic technical parameters – Nhouse-300 (NH1-030-ECS0ERxAS-xA0) – enthalpy exchanger
Tab. 2
Nhouse type |  |  | NH1-30-ECS0ERXAS-0A0 | NH1-30-ECS0ERPAS-0A0 | NH1-30-ECS0ERXAS-1A0 | NH1-30-ECS0ERPAS-1A0
Bypass version |  |  | Electronic |  | Mechanical
Unit equipment - preheater |  |  | - | electric | - | electric
Nominal air output* / BOOST** |  | m3/hour | 290/300 |  | 260/280
Noise level** |  | dB(A) | 42.9 |  | 41.5
Weight**** |  | kg | 16.6 | 17.7 | 16.5 | 17.5
Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
Nominal unit power consumption* / BOOST** |  | W | 182/192 | 782/792 | 178/179 | 778/779
Nominal unit current* / BOOST** |  | A | 1.42/1.5 | 4/4.1 | 1.4/1.4 | 4/4
Recuperation efficacy ***** | heat | % | 75 |  | 74
| humidity | % | 66 |  | 64
Protection type |  | IP | 20
Energy efficiency ratio (ERP) |  |  | cold climate A+, medium climate A, warm climate A
* Nominal air output (power, current) at an external pressure drop of 150 Pa
** BOOST regime - maximum intense ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
*** Sound pressure level in free space at the distance of 3 m
**** Unit weight without packaging
***** Recuperation efficiency per EN 308

## 2.2. - Tab. 3,4
NH1-030-ECS0HRxAS-0A0 – heat exchanger, electronic bypass
Unit radiating in the interior (inside the room)
tab.3
| Degree of air output | Air output | Sound power level LWA [dB (A)] | [8 empty] | Sound pressure level in the open field on the reflection plane
|  |  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA | 1.5 m | 3 m
| LED on the controller | (m3/h) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | LPA ( dBA ) | LPA ( dBA )
| 1. | 45 | 14.3657 | 21.0215 | 26.7454 | 28.0157 | 28.8327 | 19.5586 | 10.3993 | 12.1702 | 33.2882 | <20 | <20
| 2. | 85 | 18.6185 | 33.3921 | 38.8182 | 36.0013 | 32.7577 | 26.5211 | 13.3155 | 12.3579 | 42.1011 | 23.3 | <20
| 3. | 125 | 32.0437 | 38.0124 | 50.4731 | 44.5231 | 41.676 | 38.3133 | 24.5555 | 15.4879 | 52.2944 | 33.5 | 28.4
| 4. | 170 | 35.3621 | 40.557 | 56.3722 | 50.5257 | 47.5086 | 46.2567 | 34.2199 | 21.6213 | 58.2164 | 39.4 | 34.4
| 5. | 210 | 37.3238 | 45.5202 | 60.6818 | 57.8339 | 53.4127 | 51.8677 | 42.1938 | 29.192 | 63.4418 | 44.6 | 39.6
| 6. | 250 | 48.1101 | 50.066 | 59.5604 | 64.6842 | 58.3407 | 56.1323 | 48.1234 | 35.5403 | 67.1365 | 48.3 | 43.3
| 7. - Nominal | 300 | 46.7001 | 50.5799 | 62.0492 | 66.0461 | 62.1057 | 60.0189 | 52.3952 | 40.1616 | 69.3453 | 50.5 | 45.5
| 8. boost | 310 | 46.2549 | 50.5177 | 61.809 | 66.834 | 62.0573 | 59.9587 | 52.3324 | 40.1252 | 69.6724 | 50.9 | 45.8
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
Unit radiates into the duct - nominal air output
tab.4
| Connecting sockets | Sound power level LWA [dB (A)]
|  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA
|  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA)
| ODA | 48.5458 | 54.5956 | 54.5671 | 65.5552 | 58.6279 | 47.1997 | 37.5376 | 26.7389 | 67.0132
| SUP | 53.0269 | 63.2941 | 60.8634 | 70.0877 | 63.1198 | 59.6371 | 54.6846 | 42.7432 | 72.3156
| ETA | 51.0071 | 53.9139 | 55.3306 | 66.358 | 56.8799 | 45.9596 | 37.7356 | 25.6352 | 67.4585
| EHA | 51.863 | 61.9416 | 60.9419 | 77.6676 | 66.2631 | 60.9333 | 55.9957 | 43.6685 | 78.2799

## 2.2. - Tab. 5,6
NH1-030-ECS0HRxAS-1A0 - heat exchanger, mechanical bypass
Unit radiating in the interior (inside the room
Tab. 5
| Air output level | Air output | Sound power level LWA [dB (A)] | [8 empty] | Sound pressure level in the open field on the reflection plane
|  |  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA | 1.5 m | 3 m
| LED on the controller | (m3/h) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | LPA ( dBA ) | LPA ( dBA )
| 1. | 40 | 13.5196 | 20.7132 | 25.252 | 27.1985 | 26.5737 | 17.2266 | 7.8362 | 9.3974 | 31.9629 | <20 | <20
| 2. | 75 | 17.7724 | 33.0837 | 37.3249 | 35.1841 | 30.4988 | 24.1892 | 10.7524 | 9.5851 | 40.7758 | 21.98 | <20
| 3. | 115 | 31.1976 | 37.7041 | 48.9797 | 43.7059 | 39.4171 | 35.9814 | 21.9925 | 12.7151 | 50.9691 | 32.18 | 27.08
| 4. | 155 | 34.5161 | 40.2487 | 54.8789 | 49.7086 | 45.2496 | 43.9248 | 31.6568 | 18.8485 | 56.8911 | 38.08 | 33.08
| 5. | 195 | 36.4777 | 45.2118 | 59.1885 | 57.0167 | 51.1537 | 49.5358 | 39.6307 | 26.4192 | 62.1165 | 43.28 | 38.28
| 6. | 230 | 47.2641 | 49.7576 | 58.067 | 63.867 | 56.0817 | 53.8004 | 45.5604 | 32.7675 | 65.8112 | 46.98 | 41.98
| 7. - Nominal | 270 | 45.854 | 50.2716 | 60.5559 | 65.2289 | 59.8467 | 57.687 | 49.8321 | 37.3888 | 68.02 | 49.18 | 44.18
| 8. boost | 290 | 45.4089 | 50.2093 | 60.3157 | 66.0168 | 59.7984 | 57.6268 | 49.7693 | 37.3524 | 68.3471 | 49.58 | 44.48
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
Unit radiates into the duct - nominal air output
tab.6
| Connecting sockets | Sound power level LWA [dB (A)]
|  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA
|  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA)
| ODA | 47.6998 | 54.2873 | 53.0737 | 64.738 | 56.3689 | 44.8678 | 34.9746 | 23.9661 | 65.6879
| SUP | 52.1808 | 62.9858 | 59.37 | 69.2705 | 60.8609 | 57.3051 | 52.1215 | 39.9705 | 70.9903
| ETA | 50.161 | 53.6055 | 53.8373 | 65.5408 | 54.6209 | 43.6277 | 35.1726 | 22.8624 | 66.1333
| EHA | 51.0169 | 61.6332 | 59.4486 | 76.8504 | 64.0041 | 58.6013 | 53.4326 | 40.8957 | 76.9547

## 2.2. - Tab. 7,8
NH1-030-ECS0ERxAS-0A0 - enthalpy exchanger, electronic bypass
Unit radiating in the interior (inside the room
tab.7
| Degree of air output | Air output | Sound power level LWA [dB (A)] | [8 empty] | Sound pressure level in the open field on the reflection plane
|  |  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA | 1.5 m | 3 m
| LED on the controller | (m3/h) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | LPA ( dBA ) | LPA ( dBA )
| 1. | 45 | 14.0837 | 20.9188 | 26.2476 | 27.7433 | 28.0797 | 18.7813 | 9.5449 | 11.2459 | 32.8464 | <20 | <20
| 2. | 80 | 18.3364 | 33.2893 | 38.3205 | 35.7289 | 32.0048 | 25.7438 | 12.4611 | 11.4336 | 41.6594 | 22.86 | <20
| 3. | 120 | 31.7617 | 37.9096 | 49.9753 | 44.2507 | 40.9231 | 37.536 | 23.7012 | 14.5636 | 51.8527 | 33.06 | 27.96
| 4. | 165 | 35.0801 | 40.4543 | 55.8744 | 50.2534 | 46.7556 | 45.4794 | 33.3655 | 20.6971 | 57.7746 | 38.96 | 33.96
| 5. | 205 | 37.0418 | 45.4174 | 60.184 | 57.5615 | 52.6597 | 51.0904 | 41.3394 | 28.2678 | 63 | 44.16 | 39.16
| 6. | 245 | 47.8281 | 49.9632 | 59.0626 | 64.4118 | 57.5877 | 55.355 | 47.2691 | 34.616 | 66.6947 | 47.86 | 42.86
| 7. - Nominal | 290 | 46.418 | 50.4771 | 61.5515 | 65.7737 | 61.3527 | 59.2416 | 51.5408 | 39.2374 | 68.9035 | 50.06 | 45.06
| 8. boost | 300 | 45.9729 | 50.4149 | 61.3112 | 66.5616 | 61.3043 | 59.1814 | 51.478 | 39.2009 | 69.2306 | 50.46 | 45.36
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
- Unit radiates into the duct - nominal air output
tab.8
| Connecting sockets | Sound power level LWA [dB (A)]
|  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA
|  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA)
| ODA | 48.2638 | 54.4928 | 54.0693 | 65.2828 | 57.8749 | 46.4224 | 36.6833 | 25.8147 | 66.5714
| SUP | 52.7449 | 63.1914 | 60.3656 | 69.8153 | 62.3668 | 58.8597 | 53.8302 | 41.819 | 71.8738
| ETA | 50.725 | 53.8111 | 54.8329 | 66.0856 | 56.1269 | 45.1823 | 36.8813 | 24.7109 | 67.0168
| EHA | 51.581 | 61.8388 | 60.4442 | 77.3952 | 65.5101 | 60.1559 | 55.1413 | 42.7442 | 77.8382

## 2.2. - Tab. 9,10
NH1-030-ECS0ERxAS-1A0 - enthalpy exchanger, mechanical bypass
Unit radiating in the interior (inside the room
tab.9
| Degree of air output | Air output | Sound power level LWA [dB (A)] | [8 empty] | Sound pressure level in the open field on the reflection plane
|  |  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA | 1.5 m | 3 m
| LED on the controller | (m3/h) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | LPA ( dBA ) | LPA ( dBA )
| 1. | 40 | 13.2376 | 20.6104 | 24.7543 | 26.9261 | 25.8207 | 16.4493 | 6.9818 | 8.4731 | 31.5212 | <20 | <20
| 2. | 70 | 17.4904 | 32.9809 | 36.8271 | 34.9117 | 29.7458 | 23.4119 | 9.8981 | 8.6608 | 40.3341 | 21.54 | <20
| 3. | 110 | 30.9156 | 37.6013 | 48.482 | 43.4336 | 38.6641 | 35.204 | 21.1381 | 11.7908 | 50.5274 | 31.74 | 26.64
| 4. | 150 | 34.2341 | 40.1459 | 54.3811 | 49.4362 | 44.4966 | 43.1475 | 30.8024 | 17.9243 | 56.4494 | 37.64 | 32.64
| 5. | 190 | 36.1957 | 45.1091 | 58.6907 | 56.7443 | 50.4007 | 48.7585 | 38.7763 | 25.495 | 61.6747 | 42.84 | 37.84
| 6. | 225 | 46.9821 | 49.6549 | 57.5693 | 63.5946 | 55.3287 | 53.0231 | 44.706 | 31.8432 | 65.3695 | 46.54 | 41.54
| 7. - Nominal | 260 | 45.572 | 50.1688 | 60.0581 | 64.9565 | 59.0937 | 56.9097 | 48.9778 | 36.4646 | 67.5782 | 48.74 | 43.74
| 8. boost | 280 | 45.1269 | 50.1065 | 59.8179 | 65.7444 | 59.0454 | 56.8495 | 48.9149 | 36.4281 | 67.9054 | 49.14 | 44.04
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
- Unit radiates into the duct - nominal air output
tab.10
| Connecting sockets | Sound power level LWA [dB (A)]
|  | 63 | 125 | 250 | 500 | 1 | 2 | 4 | 8 | LWA
|  | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA) | (dBA)
| ODA | 47.4177 | 54.1845 | 52.576 | 64.4656 | 55.6159 | 44.0905 | 34.1202 | 23.0419 | 65.2462
| SUP | 51.8988 | 62.883 | 58.8723 | 68.9981 | 60.1079 | 56.5278 | 51.2672 | 39.0462 | 70.5486
| ETA | 49.879 | 53.5027 | 53.3395 | 65.2684 | 53.8679 | 42.8504 | 34.3182 | 21.9381 | 65.6915
| EHA | 50.7349 | 61.5304 | 58.9508 | 76.578 | 63.2511 | 57.824 | 52.5783 | 39.9714 | 76.5129

## 2.3. - Tab. 11
Heat and moisture recovery efficiency
NH1-030-ECS0HRxAS-xA0 - Heat exchanger
Tab. 11
| Series |  | Nhouse-300-efficiency of heat recovery - HRV
| Unit type |  | NH1-30-ECS0HRxAS-0A0 |  |  |  | NH1-30-ECS0HRxAS-1A0
| Bypass type |  | Electronic |  |  |  | Mechanical
|  |  | FLOW RATE (m3/hr) | Temperature % efficiency (EN308) | Current (A) | Power supply (W) | FLOW RATE (m3/hr) | Temperature % efficiency (EN308) | Current (A) | Power supply (W)
| Degree of air output | 1. | 45 | 92 | 0.1557 | 9.3061 | 40 | 91 | 0.1542 | 9.3061
|  | 2. | 85 | 88.3 | 0.1877 | 15.2245 | 75 | 87.5 | 0.18 | 14
|  | 3. | 125 | 85.1 | 0.2577 | 26.449 | 115 | 83.9 | 0.2568 | 25.2245
|  | 4. | 170 | 82.1 | 0.4037 | 46.8571 | 155 | 81.4 | 0.387 | 46.2449
|  | 5. | 210 | 80.7 | 0.6437 | 78.6939 | 195 | 79.5 | 0.63 | 76.6531
|  | 6. | 250 | 79.3 | 0.9437 | 122.3673 | 230 | 78.1 | 0.9 | 117.0612
|  | 7. - nominal | 300 | 77.8 | 1.4377 | 183.5918 | 270 | 77 | 1.37 | 180
|  | 8. BOOST* | 310 | 77.5 | 1.52 | 195 | 290 | 76.4 | 1.42 | 182
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)

## 2.3. - Tab. 12
NH1-030-ECS0ERxAS-xA0 - enthalpy exchanger
Tab. 12
Series |  | Nhouse-300-efficiency of heat and humidity recovery - ERV
Unit type |  | NH1-30-ECS0ERxAS-0A0 |  |  |  |  | NH1-30-ECS0ERxAS-1A0
Bypass type |  | Electronic |  |  |  |  | Mechanical
|  | Flow rate (m3/h) | Temperature % efficiency (EN308) | Humidity efficiency % (EN308) | Current (A) | Power supply (W) | Flow rate (m3/h) | Temperature % efficiency (EN308) | Humidity efficiency % (EN308) | Current (A) | Power supply (W)
Degree of air output | 1. | 45 | 92 | 88 | 0.14 | 8.0816 | 40 | 83 | 76.1 | 0.1542 | 9
| 2. | 80 | 86.2 | 83.9 | 0.18 | 14.2041 | 70 | 81.1 | 73.1 | 0.18 | 12.9796
| 3. | 120 | 83 | 79.2 | 0.26 | 26.449 | 110 | 79.3 | 68.2 | 0.2568 | 25.2245
| 4. | 165 | 80.2 | 72.1 | 0.41 | 48 | 150 | 77 | 65.4 | 0.387 | 45.2449
| 5. | 205 | 77.1 | 69.8 | 0.63 | 77.4694 | 190 | 75.1 | 63.1 | 0.63 | 75.4286
| 6. | 245 | 75 | 64 | 0.94 | 122 | 225 | 72 | 59.2 | 0.9 | 116.6939
| 7. - nominal | 290 | 73.2 | 59.1 | 1.42 | 181.551 | 260 | 70.5 | 55.2 | 1.37 | 177.9592
| 8. BOOST* | 300 | 72.1 | 57 | 1.5 | 192 | 280 | 68.1 | 53 | 1.42 | 179
* BOOST mode - intensive ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)

## 3.3.2.3. - Tab. 13
Tab. 13
Unit type |  | Circuit breaker capacity | Number of phases x voltage
Nhouse 300 | NH1-30-ECS0HRXxx-0A0 | 10 | 1x230V
NH1-30-ECS0HRPxx-0A0
NH1-30-ECS0HRXxx-1A0
NH1-30-ECS0HRPxx-1A0

## 5.4.2. - Tab. 14
Description of the functions of the control buttons
Tab. 14
Control description number | Symbol | Button/ Indication | Button description | Active in mode / number of clicks |  |  | Function | Note
|  |  |  | Dormant | Control | Settings
|  |  |  | 0x | 1x | 2x
1. |  | Button | Reduction of ventilation output |  |  |  | - Switches from the control regime to the ventilation output setting regime - Press the button to reduce the desired level by one step on the ventilation output setting scale
2. |  | Button | Unit switching on (signalling)/switching off ON/OFF |  |  |  | - By holding the button for 3 seconds, switch the unit on (LED lights up) or off - if the LED flashes after the unit is switched off, the heating is cooled down. Once finished, it will turn off
3. |  | Toggle function button | Start of intensive ventilation - BOOST |  |  |  | - Press the button for 3sec to start intensive ventilation for 1 min. To switch it off before 10 minutes pass, press the button again for 3 seconds, and the ventilation returns to the pre-start regime. | - The function start indication is flashing diode 12. - The air output for intensive ventilation and the running time in the boost regime is set in the customer menu 5.5.
|  |  | Increasing the level of ventilation output |  |  |  | - Switches from control regime to the ventilation output setting regime - Press the button to increase the demand on the ventilation output setting scale
4. |  | Status indication button | Switching between automatic mode (signalling) and manual mode |  |  |  | - The factory setting is the manual regime, request for continuous ventilation - ventilation is operated at user request, ignores requests from AQS sensors - indicator light is not lit - Press to activate automatic mode, ventilation on demand - ventilation is operated according to the AQS sensor requests - the light is on | - If you activate the automatic regime, and the light at the button flashes 3 times and returns to the manual regime - no AQS sensors are attached
5. |  | Status indication | Filter clogged indication |  |  |  | - The clogged filter indication is triggered after approx. 6 months of unit operation (only if the unit is ventilating). - The indication is expressed by a flashing red LED. | - Replace and reset the filter according to Section 6.
6. |  | Double-function and status indication button | Night cooling - on (signalling)/off |  |  |  | - Press the button to start the night cooling function. Night cooling is used to cool the ventilated area in the summer with night cold air. The function is active for 8 hours from pressing the button. - The intensity of the supplied air can be changed even when the function is activated. When the function is completed, the values return to the settings before the function started. | - It is recommended to activate the function after 10 p.m. During the summer months, the air is coldest around 5 a.m.
|  |  | Child lock |  |  |  | - protection against manipulation by unauthorised persons. It is activated/deactivated by pressing the button for more than 6 sec. Activation/deactivation is indicated by 3 flashes of all the status LEDs | - When attempting to change the parameters during the activated function, all the status LEDs flash once
10. |  | Status indication | Ventilation operation status diode |  |  |  | - In the control regime, the diode is lit - unit is ventilating - In the setting regime, the diode flashes - you are in the required ventilation output setting regime - Ventilation can be switched off. In the setting mode, reduce the output (button 1) until the last diode on the range turns off. | You can use the fan shutdown e.g.: in the summer - you do not wish to ventilate normally, but you wish to turn on night cooling to cool down the building that the unit serves

## 5.4.3. - Tab. 15
Description of the ventilation output setting scale
Control description number | Symbol | Display description | Note
11. |  | Indication of 7 ventilation levels. The LEDs are switched on and off gradually, as required by the user | The setting values are provided in Tab.19.
12. |  | Signalling by flashing LED for 1 min - intensive ventilation function started - can be adjusted in the customer menu | If the intensive ventilation function is activated, the entire range for setting the ventilation level is also lit.

## 5.4.3. - Tab. 16
Unit output settings
Tab. 16
Displayed LED on the controller range | Recuperation exchanger - HRV |  | Recuperation exchanger - ERV
| Electronic bypass | Mechanical bypass | Electronic bypass | Mechanical bypass
| NH1-30-ECS0HRXAS-0A0 | NH1-30-ECS0HRXAS-1A0 | NH1-30-ECS0ERXAS-0A0 | NH1-30-ECS0ERXAS-1A0
| m3/h* | m3/h* | m3/h* | m3/h*
1. | 45 | 40 | 45 | 40
2. | 85 | 75 | 80 | 70
3. | 125 | 115 | 120 | 110
4. | 170 | 155 | 165 | 150
5. | 210 | 195 | 205 | 190
6. | 250 | 230 | 245 | 225
7. | 300 | 270 | 290 | 260
8. - BOOST* | 310 | 290 | 300 | 280
* Air outputs are given at the external pressure drop of 150 Pa per the nominal flow (stage 7)
** BOOST regime - maximum intense ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)

## 5.4.5. - Picture 42.
5.4.7. Display of the LED Indicated Statuses on the Controller
Blue LED range diode - ventilation level - 11; 12
| Status LED - fan - 10. |  |  | - shine - shows the selected ventilation level
| Blue |  |  | - LED 1; 2; 3; 4 flashing - supply fan failure
| - shine - fan operation |  |  | - LED 5; 6; 7; 8 flashing - exhaust fan failure
| - flashing - in the fan power setting mode |  |  | - LED 3; 4; 5; 6 flashing - “anti-freeze” sensor failure
Blue LED status diode - ON/OFF
- shine - the unit controller - ON
- flashes – cooling mode after switching off the control
| Blue LED status diode - automatic (AQS) |  |  | Blue LED status diode - summer mode - 6.
| / manual (depending on the user) - 4. |  |  | - shine - function activated
| - shine - automatic mode ON (AQS) |  |  | - Flashes 3 times - function inactive - poor ambient
| - Flashing - reading a number |  |  | conditions
- Flashes 3 times and then goes out - no sensor (AQS)
Red LED status diode - filter clogging - 5.
- flashing - indicates filter clogging
|  | Common functions for all the blue status diodes | - 3 flashes for activation and deactivation of the "child lock" function
- 1 flash for indicating that the "child lock” function is active
- 3 flashes when starting the BOOST function - cannot be activated - low outdoor temperature

## 5.5.2. - Tab. 17
BOOST regime air output setting level
Recovery exchanger type | Bypass type | Unit type | Displayed LED on the controller range
|  |  | 1+2 | 3+4 | 5+6 | 7+8
|  |  | m3/h* | m3/h* | m3/h* | m3/h*
HRV | Electronic | NH1-30-ECS0HRxAS-0A0 | 210 | 250 | 300 | 310
| Mechanical | NH1-30-ECS0HRxAS-1A0 | 195 | 230 | 270 | 290
ERV | Electronic | NH1-30-ECS0ERxAS-0A0 | 205 | 245 | 290 | 300
| Mechanical | NH1-30-ECS0ERxAS-1A0 | 190 | 225 | 260 | 280
* Air outputs are given at an external pressure drop of 150 Pa per the nominal flow rate
Highlighted values - factory settings

## 5.5.3. - Tab.18
Options for setting the running time in the BOOST regime
Displayed LED on the controller range | 1. | 2. | 3. | 4.
Running time in the BOOST regime | 0.5 | 1 | 2 | 4
Displayed LED on the controller range | 5. | 6. | 7. | 8.
Running time in the BOOST regime | 7 | 10 | 15 | 20
Highlighted value - factory setting

## 5.5.4. - Tab.19
Options for setting the fan distribution
Displayed LED on the controller range | 1. | 2. | 3. | 4.
% fan distribution | 0% - equal pressure | 5 | 10 | 15
Displayed LED on the controller range | 5. | 6. | 7. | 8.
% fan distribution | 20 | 25 | 30 | 35
Highlighted value - factory setting

## Technical parameters - Quick
- Basic technical parameters – Quick
| Heat recuperation exchanger - HRV |  |  | NH1-30-ECS0HRXAS-0A0 | NH1-30-ECS0HRPAS-0A0 | NH1-30-ECS0HRXAS-1A0 | NH1-30-ECS0HRPAS-1A0
| Bypass version |  |  | Electronic |  | Mechanical
| Unit equipment - preheater |  |  | - | electric | - | electric
| Nominal air output* / BOOST** |  | m3/hour | 300/310 |  | 270/290
| Noise level** |  | dB(A) | 43.3 |  | 42
| Weight**** |  | kg | 16.1 | 17.2 | 16 | 17
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal unit power consumption* / BOOST** |  | W | 184/195 | 784/795 | 180/182 | 780/782
| Nominal unit current* / BOOST** |  | A | 1.44/1.52 | 4.04/4.12 | 1.4/1.4 | 4/4
| Recuperation efficacy ***** |  | % | 81 |  | 80.5
| Protection type |  | IP | 20
| Energy efficiency ratio (ERP) |  |  | cold climate A+, medium climate A, warm climate A
| Enthalpy heat exchanger - ERV |  |  | NH1-30-ECS0ERXAS-0A0 | NH1-30-ECS0ERPAS-0A0 | NH1-30-ECS0ERXAS-1A0 | NH1-30-ECS0ERPAS-1A0
| Bypass version |  |  | Electronic |  | Mechanical
| Unit equipment - preheater |  |  | - | electric | - | electric
| Nominal air output* / BOOST** |  | m3/hour | 290/300 |  | 260/280
| Noise level** |  | dB(A) | 42.9 |  | 41.5
| Weight**** |  | kg | 16.6 | 17.7 | 16.5 | 17.5
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal unit power consumption* / BOOST** |  | W | 182/192 | 782/792 | 178/179 | 778/779
| Nominal unit current* / BOOST** |  | A | 1.42/1.5 | 4/4.1 | 1.4/1.4 | 4/4
| Recuperation efficacy ***** | heat | % | 75 |  | 74
|  | humidity | % | 66 |  | 64
| Protection type |  | IP | 20
| Energy efficiency ratio (ERP) |  |  | cold climate A+, medium climate A, warm climate A
* Nominal air output (power, current) at an external pressure drop of 150 Pa
** BOOST regime - maximum intense ventilation for a set period of time (ventilation intensity and ventilation time can be set in the customer menu)
*** Sound pressure level in free space at the distance of 3 m
**** Unit weight without packaging
***** Recuperation efficiency per EN 308

## 8.1. - Tab.20
- error messages - troubleshooting
Error No. | Error, fault message |  | Possible cause of failure | Troubleshooting
1. | The unit does not start |  | The power cable is not connected | - check the mains connection - check the activation of the safety element
|  |  | The main switch is in position 0 | - set the switch to position I
|  |  | The entire controller loading process did not take place | - Switch the unit off with the main switch and switch it on again, wait until the controller has finished loading - the controller stops flashing
|  |  | Hold down button 2 (ON/OFF) for a short time, approx. 3 sec | - hold down button 2 (ON/OFF) until the LED above the button lights up
2. | The unit does not start when first put into operation - LED above button 2 is lit |  | The demand for ventilation and heating is switched off | - Enter the unit setup regime and check the ventilation output request settings - Make the settings per chapter 5.4.2. table 14
3. | Red indicator light above the FILTER sign is flashing |  | Filter clogging indication | - replace the filter according to Section 6.
4. | No or low ventilation output even when the unit is set to the maximum power |  | Clogged filter | - replace the filter according to Section 6.
|  |  | Contaminated - blocked piping, unit outlets | - Inspect the piping. Clean the unit per chapter 7.
5. | Unit started to be too noisy |  | Clogged filter | - replace the filter according to Section 6.
|  |  | Fan distribution wrongly set | - Check and re-set the fan distribution per chapter 5.5.4.
|  |  | Defective motor bearing | - contact the unit supplier
6. | Electrical heating of the unit does not heat |  | Clogged filter - no flow | - replace the filter according to Section 6.
|  |  | Contaminated - blocked piping, unit outlets | - Check and clean the unit according to Section 7.
|  |  | activated heat exchanger protection against overheating | - switch off the unit with the main switch. Turn the unit on again after 5 minutes (reset of protection). If the problem persists, contact the unit supplier
7. | Unable to activate the night cooling function - bypass (button 6) - The button signalling flashes 3 times and the function does not switch on |  | Function start requirements are not met - outside temperature too low | - Wait for the outside temperature to rise. The function is active only at summer temperatures.
8. | The night cooling function cannot be switched on (button 6.) - all the status diodes flash once (at buttons 6, 4, 7, 10), the function does not switch on |  | BOOST function active | - Wait for the BOOST regime to end - Switch off the BOOST function per chapter 4.2.4.
|  |  | Active child lock function | - Switch off the child lock function per chapter 5.4.2. Tab. 14
9. | The BOOST mode cannot be switched on - status diodes flash once or 3 times (at buttons 6, 4, 7, 10), the function does not switch on |  | 3 flashes - very low outdoor temperature | - wait for the outdoor temperature to rise
|  |  | 1 flash - child lock function is active | - Switch off the child lock function per chapter 5.4.2. Tab. 14
10. | The automatic mode cannot be started - when the button 4 is pressed, the indicator flashes 3 times or lights |  | 3 flashes - unit is not fitted with any AQS sensor | - You have no AQS sensor connected. - Check the AQS sensor wiring
11. | When any button is pressed, the status diodes flash once (at buttons 6, 4, 7, 10) |  | Active child lock function | - Switch off the child lock function per chapter 5.4.2. Tab. 14
12. | The unit is inoperable and the 4 LEDs on the range for adjusting the ventilation power on the control panel are continuously flashing | - diodes 1; 2; 3; 4 are flashing | Supply fan failure | - Switch off the unit at the control panel and main switch, leave the unit off for approx. 10 sec - restart the unit - If the error persists after restarting the unit, contact the unit supplier
13. |  | - diodes 5; 6; 7; 8 are flashing | Exhaust fan failure
14. |  | - diodes 3; 4; 5; 5 are flashing | Faulty anti-freeze sensor